## Table 1
CHAPTER 9 TABLES
Table 9 Alternating-Current Resistance and Reactance for 600-Volt Cables, 3-Phase,
60 Hz, 75°C (167°F) — Three Single Conductors in Conduit
Size (AWG or kcmil) | Ohms to Neutral per Kilometer Ohms to Neutral per 1000 Feet | [13 empty] | Size (AWG or kcmil)
| XL (Reactance) for All Wires |  | Alternating-Current Resistance for Uncoated Copper Wires |  |  | Alternating-Current Resistance for Aluminum Wires |  |  | EffectiveZat 0.85PF for Uncoated Copper Wires |  |  | EffectiveZat 0.85PF for Aluminum Wires
| PVC, Alum- inum Conduits | Steel Conduit | PVC Conduit | Alum- inum Conduit | Steel Conduit | PVC Conduit | Alum- inum Conduit | Steel Conduit | PVC Conduit | Alum- inum Conduit | Steel Conduit | PVC Conduit | Alum- inum Conduit | Steel Conduit
14 | 0.190 0.058 | 0.240 0.073 | 10.2 3.1 | 10.2 3.1 | 10.2 3.1 |  |  |  | 8.9 2.7 | 8.9 2.7 | 8.9 2.7 |  |  |  | 14
12 | 0.177 0.054 | 0.223 0.068 | 6.6 2.0 | 6.6 2.0 | 6.6 2.0 | 10.5 3.2 | 10.5 3.2 | 10.5 3.2 | 5.6 1.7 | 5.6 1.7 | 5.6 1.7 | 9.2 2.8 | 9.2 2.8 | 9.2 2.8 | 12
10 | 0.164 0.050 | 0.207 0.063 | 3.9 1.2 | 3.9 1.2 | 3.9 1.2 | 6.6 2.0 | 6.6 2.0 | 6.6 2.0 | 3.6 1.1 | 3.6 1.1 | 3.6 1.1 | 5.9 1.8 | 5.9 1.8 | 5.9 1.8 | 10
8 | 0.171 0.052 | 0.213 0.065 | 2.56 0.78 | 2.56 0.78 | 2.56 0.78 | 4.3 1.3 | 4.3 1.3 | 4.3 1.3 | 2.26 0.69 | 2.26 0.69 | 2.30 0.70 | 3.6 1.1 | 3.6 1.1 | 3.6 1.1 | 8
6 | 0.167 0.051 | 0.210 0.064 | 1.61 0.49 | 1.61 0.49 | 1.61 0.49 | 2.66 0.81 | 2.66 0.81 | 2.66 0.81 | 1.44 0.44 | 1.48 0.45 | 1.48 0.45 | 2.33 0.71 | 2.36 0.72 | 2.36 0.72 | 6
4 | 0.157 0.048 | 0.197 0.060 | 1.02 0.31 | 1.02 0.31 | 1.02 0.31 | 1.67 0.51 | 1.67 0.51 | 1.67 0.51 | 0.95 0.29 | 0.95 0.29 | 0.98 0.30 | 1.51 0.46 | 1.51 0.46 | 1.51 0.46 | 4
3 | 0.154 0.047 | 0.194 0.059 | 0.82 0.25 | 0.82 0.25 | 0.82 0.25 | 1.31 0.40 | 1.35 0.41 | 1.31 0.40 | 0.75 0.23 | 0.79 0.24 | 0.79 0.24 | 1.21 0.37 | 1.21 0.37 | 1.21 0.37 | 3
2 | 0.148 0.045 | 0.187 0.057 | 0.62 0.19 | 0.66 0.20 | 0.66 0.20 | 1.05 0.32 | 1.05 0.32 | 1.05 0.32 | 0.62 0.19 | 0.62 0.19 | 0.66 0.20 | 0.98 0.30 | 0.98 0.30 | 0.98 0.30 | 2
1 | 0.151 0.046 | 0.187 0.057 | 0.49 0.15 | 0.52 0.16 | 0.52 0.16 | 0.82 0.25 | 0.85 0.26 | 0.82 0.25 | 0.52 0.16 | 0.52 0.16 | 0.52 0.16 | 0.79 0.24 | 0.79 0.24 | 0.82 0.25 | 1
1/0 | 0.144 0.044 | 0.180 0.055 | 0.39 0.12 | 0.43 0.13 | 0.39 0.12 | 0.66 0.20 | 0.69 0.21 | 0.66 0.20 | 0.43 0.13 | 0.43 0.13 | 0.43 0.13 | 0.62 0.19 | 0.66 0.20 | 0.66 0.20 | 1/0
2/0 | 0.141 0.043 | 0.177 0.054 | 0.33 0.10 | 0.33 0.10 | 0.33 0.10 | 0.52 0.16 | 0.52 0.16 | 0.52 0.16 | 0.36 0.11 | 0.36 0.11 | 0.36 0.11 | 0.52 0.16 | 0.52 0.16 | 0.52 0.16 | 2/0
3/0 | 0.138 0.042 | 0.171 0.052 | 0.253 0.077 | 0.269 0.082 | 0.259 0.079 | 0.43 0.13 | 0.43 0.13 | 0.43 0.13 | 0.289 0.088 | 0.302 0.092 | 0.308 0.094 | 0.43 0.13 | 0.43 0.13 | 0.46 0.14 | 3/0
4/0 | 0.135 0.041 | 0.167 0.051 | 0.203 0.062 | 0.220 0.067 | 0.207 0.063 | 0.33 0.10 | 0.36 0.11 | 0.33 0.10 | 0.243 0.074 | 0.256 0.078 | 0.262 0.080 | 0.36 0.11 | 0.36 0.11 | 0.36 0.11 | 4/0
250 | 0.135 0.041 | 0.171 0.052 | 0.171 0.052 | 0.187 0.057 | 0.177 0.054 | 0.279 0.085 | 0.295 0.090 | 0.282 0.086 | 0.217 0.066 | 0.230 0.070 | 0.240 0.073 | 0.308 0.094 | 0.322 0.098 | 0.33 0.10 | 250
300 | 0.135 0.041 | 0.167 0.051 | 0.144 0.044 | 0.161 0.049 | 0.148 0.045 | 0.233 0.071 | 0.249 0.076 | 0.236 0.072 | 0.194 0.059 | 0.207 0.063 | 0.213 0.065 | 0.269 0.082 | 0.282 0.086 | 0.289 0.088 | 300
350 | 0.131 0.040 | 0.164 0.050 | 0.125 0.038 | 0.141 0.043 | 0.128 0.039 | 0.200 0.061 | 0.217 0.066 | 0.207 0.063 | 0.174 0.053 | 0.190 0.058 | 0.197 0.060 | 0.240 0.073 | 0.253 0.077 | 0.262 0.080 | 350
400 | 0.131 0.040 | 0.161 0.049 | 0.108 0.033 | 0.125 0.038 | 0.115 0.035 | 0.177 0.054 | 0.194 0.059 | 0.180 0.055 | 0.161 0.049 | 0.174 0.053 | 0.184 0.056 | 0.217 0.066 | 0.233 0.071 | 0.240 0.073 | 400
70–722
NATIONAL ELECTRICAL CODE 2011 Edition

## Table 2
TABLES CHAPTER 9
Table 9Continued
Size (AWG or kcmil) | Ohms to Neutral per Kilometer Ohms to Neutral per 1000 Feet | [15 empty] | Size (AWG or kcmil)
| XL (Reactance) for All Wires |  | Alternating-Current Resistance for Uncoated Copper Wires |  |  |  | Alternating-Current Resistance for Aluminum Wires |  |  | EffectiveZat 0.85PF for Uncoated Copper Wires |  |  | EffectiveZat 0.85PF for Aluminum Wires
| PVC, Alum- inum Conduits | Steel Conduit | PVC Conduit | Alum- inum Conduit | Steel Conduit |  | PVC Conduit | Alum- inum Conduit | Steel Conduit | PVC Conduit | Alum- inum Conduit | Steel Conduit | PVC Conduit |  | Alum- inum Conduit | Steel Conduit
500 | 0.128 0.039 | 0.157 0.048 | 0.089 0.027 | 0.105 0.032 | 0.095 0.029 |  | 0.141 0.043 | 0.157 0.048 | 0.148 0.045 | 0.141 0.043 | 0.157 0.048 | 0.164 0.050 | 0.187 0.057 |  | 0.200 0.061 | 0.210 0.064 | 500
600 | 0.128 0.039 | 0.157 0.048 | 0.075 0.023 | 0.092 0.028 | 0.082 0.025 |  | 0.118 0.036 | 0.135 0.041 | 0.125 0.038 | 0.131 0.040 | 0.144 0.044 | 0.154 0.047 | 0.167 0.051 |  | 0.180 0.055 | 0.190 0.058 | 600
750 | 0.125 0.038 | 0.157 0.048 | 0.062 0.019 | 0.079 0.024 | 0.069 0.021 |  | 0.095 0.029 | 0.112 0.034 | 0.102 0.031 | 0.118 0.036 | 0.131 0.040 | 0.141 0.043 | 0.148 0.045 |  | 0.161 0.049 | 0.171 0.052 | 750
1000 | 0.121 0.037 | 0.151 0.046 | 0.049 0.015 | 0.062 0.019 | 0.059 0.018 |  | 0.075 0.023 | 0.089 0.027 | 0.082 0.025 | 0.105 0.032 | 0.118 0.036 | 0.131 0.040 | 0.128 0.039 |  | 0.138 0.042 | 0.151 0.046 | 1000
Notes:
1. These values are based on the following constants: UL-Type RHH wires with Class B stranding, in cradled conﬁgu- ration. Wire conductivities are 100 percent IACS copper and 61 percent IACS aluminum, and aluminum conduit is 45 percent IACS. Capacitive reactance is ignored, since it is negligible at these voltages. These resistance values are valid only at 75°C (167°F) and for the parameters as given, but are representative for 600-volt wire types operating at 60 Hz. 2.Effective Zis deﬁned asRcos(θ) + X sin(θ), whereθis the power factor angle of the circuit. Multiplying current
by effective impedance gives a good approximation for line-to-neutral voltage drop. Effective impedance values shown in this table are valid only at 0.85 power factor. For another circuit power factor (PF), effective impedance (Ze) can be calculated fromRandX L values given in this table as follows:Ze=R×PF+X L sin[arccos(PF)].
Table 10 Conductor Stranding
Conductor Size | [5 empty] | Number of Strands
[6 empty] | Copper | [7 empty] | Aluminum
AWG or kcmil |  |  | mm2 |  |  | Class B |  |  |  | Class C |  |  |  | Class B
24–30 |  |  | 0.20–0.05 |  |  | a |  |  |  | — |  |  |  | —
22 |  |  | 0.32 |  |  | 7 |  |  |  | — |  |  |  | —
20 |  |  | 0.52 |  |  | 10 |  |  |  | — |  |  |  | —
18 |  |  | 0.82 |  |  | 16 |  |  |  | — |  |  |  | —
16 |  |  | 1.3 |  |  | 26 |  |  |  | — |  |  |  | —
14–2 |  |  | 2.1–33.6 |  |  | 7 |  |  |  | 19 |  |  |  | 7b
1–4/0 |  |  | 42.4–107 |  |  | 19 |  |  |  | 37 |  |  |  | 19
250–500 |  |  | 127–253 |  |  | 37 |  |  |  | 61 |  |  |  | 37
600–1000 |  |  | 304–508 |  |  | 61 |  |  |  | 91 |  |  |  | 61
1250–1500 |  |  | 635–759 |  |  | 91 |  |  |  | 127 |  |  |  | 91
1750–2000 |  |  | 886–1016 |  |  | 127 |  |  |  | 271 |  |  |  | 127
aNumber of strands vary.
bAluminum 14 AWG (2.1 mm2) is not available.
With the permission of Underwriters Laboratories, Inc., material is reproduced from UL Standard 486A-B, Wire Connec- tors, which is copyrighted by Underwriters Laboratories, Inc., Northbrook, Illinois. While use of this material has been authorized, UL shall not be responsible for the manner in which the information is presented, nor for any interpretations thereof. For more information on UL or to purchase standards, please visit our Standards website at www.comm-2000.com or call 1-888-853-3503.
2011 Edition NATIONAL ELECTRICAL CODE 70–723